## Project
Project overview
Inputs
Project name: | Example SIFs - not real data
Client: | Our valued SILability user
Version number: | 0.1
Edit number: | 209
Team members: | Peter Clarke
Date initiated: | 07 Apr 2016
Outputs
Number of SIFs | 1
Number of SIL 1 achieved | 0
Number of SIL 2 achieved | 0
Number of SIL 3 achieved | 0
Number of SIL 4 achieved | 0
SIF
SIF Name | Simple 1oo1 SIF
SIF Tag | UX-501
SIF Serial Number | 1
SIF Description | On PAHH-123 (1oo1): close XV-456 (1oo1)
SIF Reference | SRS Rev 4, page 123
Unit/Process Area | New unit
Hazard | Malfunction of blanket gas regulator in tank T-100
Consequence | Pressure buildup in T-100. May be unable to transfer product to T-100, leading to loss of production.
Inputs |  |  | Units
Mode of operation | Low demand
Target SIL |  | 1
Target RRF |  | 40.0
Architectural Constraints model |  | IEC 61511:2003
Outputs |  |  | Units
SIL Achieved |  | 1
Final PFDavg for the SIF |  | 2.38e-02
Risk Reduction Factor Achieved |  | 42.0
SIL (PFDavg) |  | 1
PFDavg Contribution
- Sensor |  | 27.7 | %
- PLC |  | 3.57 | %
- Final Element |  | 68.7 | %
SIL achieved (architectural constraints) |  | 2
Spurious Trip - MTTFS |  | 61.6 | years
Sensor subsystem - Pressure detection in T-100
Inputs |  |  | Units
Sensor architecture |  | 1oo1
β among groups within subsystem |  | 0 | %
Outputs
Maximum SIL achieved |  | 2
Subsystem PFDavg |  | 6.60e-03
Hardware fault tolerance |  | 0
IEC 61508:2010-1 7.4.4.3.2 invoked |  | Not specified
PFDavg contribution
- Group 1 (PT-123 group) |  | 100 | %
MTTFS (spurious trip) |  | 671 | years
Sensor group 1 - PT-123 group
Inputs |  | Units | Outputs |  | Units
Group architecture | 1oo1 |  | Group PFDavg | 6.60e-03
PFDavg contribution
Mission time | 14 | years
Mean time to restore | 8.0 | hours | - Leg 1 | 100 | %
Proof test interval | 36 | months | MTTFS (spurious trip) | 671 | years
Proof test success rate | 95.0 | %
Proof test duration | 4.0 | hours
MTTR includes diagnostic time | Yes
Safe failures repaired within MTTR | Yes
β among legs within group | <Undefined> | %
Leg 1 - PT-123A
Inputs
(None)
Outputs |  | Units
Leg PFDavg | 6.44e-03
Safe Failure Fraction | 0.655
PFDavg Contribution
- Component 1 | 100 | %
Component | 1
Inputs |  | Units
Name | Pressure Transmitter
Equipment Type | PressureBrand 100-X (SS)
Component Architecture | 1oo1
Trip direction | High
λDDTotal | <Undefined> | FIT
λDUTotal | <Undefined> | FIT
λSDTotal | <Undefined> | FIT
λSUTotal | <Undefined> | FIT
λDHigh | 100.0 | FIT
λDLow | 400 | FIT
λDFreeze | 0 | FIT
λUHigh | 70.0 | FIT
λULow | 300 | FIT
λUFreeze | 0 | FIT
λResidual | 0 | FIT
β among Identical Components
Proof test coverage | 97 | %
Architectural Constraint Type (A/B) | B
Outputs
Component PFDavg | 6.44e-03
Safe Failure Fraction | 0.655
Logic Solver Subsystem
Inputs |  |  |  | Units
Logic Solver Name |  |  | SIS PLC
Equipment Name |  |  | SafetyBrain 147N
Logic Solver Architecture |  |  | 2oo4
Mission time |  |  | 12 | years
Mean Time to Restore |  |  | 16 | hours
MTTR includes diagnostic time |  |  | Yes
Proof Test Interval |  |  | 48 | months
Proof Test Success Rate |  |  | 99.7 | %
Proof Test Duration |  |  | 12 | hours
β (subsystem) |  |  | 5.0 | %
Safe failures detected |  |  | No
Logic solver is programmable |  |  | Yes
IEC 61508:2010-1 7.4.4.3.2 invoked |  |  | Not specified
Trip action |  |  | De-energise to trip
Safe failures repaired within MTTR |  |  | Yes
Outputs
Maximum SIL Achieved |  |  | 3
Subsystem PFDavg |  |  | 8.50e-04
PFDavg Contribution
- Power supply unit |  |  | 1.7 | %
- Motherboard (main processor card) |  |  | 97 | %
- I/O card |  |  | 1.1 | %
Spurious Trip - MTTFS |  |  | 43400 | years
Component | 1 | 2 | 3
Inputs |  |  |  | Units
Name | Power supply unit | Motherboard (main processor card) | I/O card
Equipment Type | SafetyBrain 147N-PSU20 | SafetyBrain 147N-CPU20+ | SafetyBrain 147N-FieldConnect XL1
Component Architecture | 1oo1 | 1oo1 | 1oo1
Trip action | Undefined | Undefined | Undefined
λDDTotal | 75.0 | 1500 | 600 | FIT
λDUTotal | 4.00 | 550 | 2.50 | FIT
λSDTotal | 520 | 5800 | 600 | FIT
λSUTotal | 5.00 | 42.0 | 5.00 | FIT
λDHigh | <Undefined> | <Undefined> | <Undefined> | FIT
λDLow | <Undefined> | <Undefined> | <Undefined> | FIT
λDFreeze | <Undefined> | <Undefined> | <Undefined> | FIT
λUHigh | <Undefined> | <Undefined> | <Undefined> | FIT
λULow | <Undefined> | <Undefined> | <Undefined> | FIT
λUFreeze | <Undefined> | <Undefined> | <Undefined> | FIT
λResidual | <Undefined> | <Undefined> | <Undefined> | FIT
β among Identical Components
Proof test coverage | 96 | 99 | 100 | %
Outputs
Component PFDavg | 1.90e-04 | 1.06e-02 | 1.17e-04
Safe Failure Fraction | 0.993 | 0.930 | 0.998
Final Element Subsystem - Final element for this SIF
Inputs |  |  | Units
Final Element Architecture |  | 1oo1
β among Groups within Subsystem |  | <Undefined> | %
Outputs
Maximum SIL Achieved |  | 1
Subsystem PFDavg |  | 1.63e-02
Hardware Fault Tolerance |  | 0
IEC 61508:2010-1 clause 7.4.4.3.2 invoked |  |  | Not specified
PFDavg Contribution
- Group 1 (T-100 shutdown valve group) |  | 1.63e-02
Spurious Trip - MTTFS |  | 67.9 | years
Final Element Group 1 - T-100 shutdown valve group
Inputs |  | Units | Outputs |  | Units
Group Architecture | 1oo1 |  | Group PFDavg | 1.63e-02
Mission time | 12 | years | PFDavg Contribution
Mean Time to Restore | 6.0 | hours
MTTR includes diagnostic time | Yes |  | - Leg 1 | 100 | %
Proof Test Interval | 15 | months | Spurious Trip - MTTFS | 67.9 | years
Proof Test Success Rate | 95.0 | %
Proof Test Duration | 2.0 | hours
Partial Valve Stroke Test Interval | 8.0 | months
Partial Valve Stroke Test Success Rate | 95 | %
Safe failures repaired within MTTR | Yes
β among Legs within Group | <Undefined> | %
Leg 1 - XV-456 assembly
Inputs
Use PVST | Yes
Outputs |  | Units
Leg PFDavg | 1.79e-02
Safe Failure Fraction | 0.583
PFD Contribution
- Component 1 | 21 | %
- Component 2 | 31 | %
- Component 3 | 49 | %
Component | 1 | 2 | 3
Inputs |  |  |  | Units
Name | Solenoid | Pneumatic actuator | Shutdown valve
Equipment Type | CoilMover 8000 (Spring return)
Component Architecture | 1oo1 | 1oo1 | 1oo1
Trip action | De-energise to trip | De-energise to trip | Close to trip
λDDTotal | 0 | 0 | 0 | FIT
λDUTotal | 340 | 420 | 440 | FIT
λSDTotal | 0 | 0 | 0 | FIT
λSUTotal | 1200 | 480 | 0 | FIT
λDHigh | <Undefined> | <Undefined> | <Undefined> | FIT
λDLow | <Undefined> | <Undefined> | <Undefined> | FIT
λDFreeze | <Undefined> | <Undefined> | <Undefined> | FIT
λUHigh | <Undefined> | <Undefined> | <Undefined> | FIT
λULow | <Undefined> | <Undefined> | <Undefined> | FIT
λUFreeze | <Undefined> | <Undefined> | <Undefined> | FIT
λResidual | <Undefined> | <Undefined> | <Undefined> | FIT
β among Identical Components
Proof test coverage | 90 | 85 | 70 | %
Architectural Constraint Type (A/B) | A | A | A
PVST coverage | 55 | 55 | 55 | %
Outputs
Component PFDavg | 3.72e-03 | 5.53e-03 | 8.76e-03
Safe Failure Fraction | 0.779 | 0.533 | 0